## Slide 1: Module 03
DC power transmission

## Slide 2
Converter
Converter
Inverter
Rectifier

## Slide 3
Converter
Load Flow Definition
  Positive load is defined for Inverter Case (generator convention)
  In USA a common used term is “Inverter Based Resources” (IBR)
  IBR are not only HVDC systems but all kind of generators such as:
        Wind Turbine Generators (WTG)
        PV
        ...
  An VSC-HVDC system can be an inverter and a rectifier depending on the power flow direction, in some applications the change of direction is necessary

## Slide 4
Converter Terminology IEC 62747:2014

## Slide 5
DC Load Flow Definitions
  DC equipment (incl. DC line) voltage is defined by the voltages and
  Converter sizing is defined by
  HVDC systems have bidirectional transmission capability, which means that every individual converter can be either rectifier or inverter

## Slide 6
Monopole
  DC Definitions
  Max. voltage created by converter:
  Max. equipment voltage:
  DC cables have different voltage rating

## Slide 7
Monopole
  Extending power transmission of the system
    Higher DC voltage
      Limited equipment availability
      Reliability
    Higher DC current
      Higher DC transmission line costs
      Reliability
    Installing additional monopole
      Additional converter equipment
      4 DC conductors
      Reliability

## Slide 8
Monopole  Bipole (BIP)
Bipole

## Slide 9
Bipole (BIP)
  3 conductors with 2 different types
  Bipole consists of two-poles which can transmit the power independently
  In case of a fault in one pole, the other pole can still transmit power providing redundancy in power transmission
  In case of symmetrical operation (both poles transmit the same power), no current is flowing through the DMR

## Slide 10
BIP operation modes
  Bipolar operation – Balanced mode
  Poles are running with at the same power
  No current is running through the DMR
  Losses optimized operation
  Monopolar operation
  Emergency mode operation
  System design relevant
  Bipolar operation – Unbalanced mode
  Split-Busbar
  Current running through the DMR in case of different power flow in the AC Grid
  Reduced redundancy

## Slide 11
DC Load Flow
  For DC load Flow calculation the converter can be represented as an ideal voltage source

## Slide 12
Balanced Operation

## Slide 13
Balanced Operation: Power Definition

## Slide 14
Balanced vs. Unbalanced Operation
  Balanced Mode
  Unbalanced Mode

## Slide 15
Monopolar operation
    Monopolar operation is usually for a short period of time till the reconfiguration of the system is finished
    If longer operation time is required, DMR needs to be designed accordingly

## Slide 16
System Earthing
    Earthing of the BIP system has no impact on the resulting currents and losses

## Slide 17
BIP  Rigid BIP
  3 conductors with 2 different types
  Bipole consists of two-poles which can transmit the power independently
  In case of a fault in one pole, the other pole can still transmit power providing redundancy in power transmission
  In case of symmetrical operation (both poles transmit the same power), no current is flowing through the DMR

## Slide 18
BIP  Rigid BIP
Bipole
Rigid Bipole

## Slide 19
Rigid BIP
  2 conductors of 1 type
  Bipole consists of two-poles which have to transmit the same power because the same power is flowing through the both poles
  In case of a fault in one pole, the other pole might not be able to transmit the power

## Slide 20
Rigid BIP Operation Modes
  Common-busbar operation
  Standard operation mode
  Split busbar operation
  Poles must have the same power during all operating modes (also during dynamic operation)
  Monopolar operation
  Reconfiguration takes > 1s

## Slide 21
Symmetrical Monopole (SMP)
  High impedance earth reference on the AC side
  DC Definitions
  SMP configuration can only be realized with VSC HVDC systems
  DC cables have the same voltage rating

## Slide 22
Modular Multilevel Converter (MMC)
 | 2 x Monopole | 1 x BIP | 1 x SMP
Transformers | -- | -- | ++
DC lines | -- 4 lines / 2 types 1563 A | - 3 lines / 2 types 1563 A | ++ 2 lines / 1 type 1563 A
Converters | - 4 Converters | - 4 Converters | + 2 Converters
Converter rating | + 320 kV | + 320 kV | -- 640 kV
Losses | -- | - | +
Reliability | ++ | + | --
  Power transmission parameters
    1000 MW
    320kV maximum DC line voltage
    1563A maximum current rating

## Slide 23
DC cable
  Main elements of the DC cable are:
    Insulator
      XLPE: Cross-linked polyethylene
      MI: Mass impregnated
    Conductor
      Copper
      Aluminium
  Balance between DC voltage and DC current for most economical design
  Generally it can be assumed that Insulator is cheaper than the conductor  Higher voltage rating is preferred
  Voltage levels in VSC-HVDC projects:
  80 kV Projects up to 200MW power
  200 kV TBC project voltage
  250 kV Used in one project
  320 kV Most common voltage
  400 kV Cable voltage promoted by some cable suppliers due 525 kV New Standard for power applications ≥ 2000 MW
  www.borealisgroup.com

## Slide 24
Topology comparisson
 | Symmetric Monopole | Rigid Bipole | Bipole with Metallic Return
DC conductors | 2 | 2 | 3
Power transmission in case of converter fault | 0 % | 50 % | 50 %
Power transmission in case of DC conductor fault | 0 % | 0 % | 50 %
Economical DC voltage | ≤ 400 kV | > 500 kV | > 500 kV
Costs | $ | $$ | $$$
Max. Power | 1400 MW (320 kV) 1500 MW (400 kV) | 2000 MW | 3000 MW