## Slide 1: Module 04
HVDC (VSC) Technology
2- and 3-Level Converter

## Slide 2: Converter
Converter
  The main driver for converter technology development was the railway system, which requires motor drives with adjustable speed
  The semiconductor development was driven by railway application which had several DC voltage levels in operation: 900V: Trams 1500 V: Trains 3000 V: Trains
  The IGBT developed were designed for that voltage level: 900 V  1800 V IGBT 1500 V  3300 V IGBT 3000 V  6500 V IGBT

## Slide 3: Converter (cont’d)
Converter
  The voltage class of the IGBTs are usually refer to the maximum voltage that can be applied across the terminals
  For system design the maximum steady state voltage has to be considered

## Slide 4: Converter Terminology
Converter Terminology
IEC 62747:2014

## Slide 5: Converter output voltage generation
Converter Output Voltage Generation

## Slide 6: Converter output voltage generation (cont’d)
Converter Output Voltage Generation
  The requested voltage signal is synthesized by Pulse Wide Modulation (PWM) with switching between +Udpe and -Udpe
  High switching frequency (> 2kHz) is necessary for an appropriate signal quality
  Additionally to the high switching frequency AC filters are installed
  The maximum AC output voltage that can be delivered by the converters depends on the available DC voltage, relation between AC and DC voltage is called modulation index

## Slide 7: Converter output voltage generation (cont’d)
Converter Output Voltage Generation
  The voltage can be changed only between two states
  The creation of any voltage is done by changing of the duration positive and negative voltage is applied:
  To create a smooth output a high switching frequency/small time step is required

## Slide 8
  Reference voltage
Modulation Technique
  Modulated voltage
Modulation Technique

## Slide 9: 2-level VSC-HVDC converters
2-Level VSC-HVDC converters
Series connection of IGBTs
  Connection of several hundred IGBTs in series
Central energy storage (capacitor)
  Capacitors have to be designed for the high voltage
  Capacitors are not redundant, a failure in the capacitor can cause the complete converter outage

## Slide 10: 2-level and 3-level
2-Level and 3-Level
Switching impulses
High switching impulses
HF filter requirement
Special shielding of the converter building required

## Slide 11: 2-level and 3-level (cont’d)
2-Level and 3-Level
Series connection of IGBTs
Current is flowing through all IGBTs
What happens in case of IGBT fault?  Converter must continue to operate
Fail-Safe IGBTs required

## Slide 12: 2-level and 3-level (cont’d)
2-Level and 3-Level
Fail-Safe IGBTs are IGBTs which are capable of
short circuit failure mode (SCFM)
Low resistance in SCFM
IGBT is capable to operate in short circuit till the next maintenance cycle
Innovative Metal System for IGBT Press Pack Modules
S. Gunturi, J. Assal, D. Schneider, S. Eicher
ISPSD, April 2003, Cambridge, England

## Slide 13: 3-level VSC-HVDC converters
3-Level VSC-HVDC converters
3-Level VSC-HVDC converters were used in some projects
Advantage of the technology is the reduced harmonic content
The technology was replaced by 2-Level converters with Optimized PWM (OPWM)

## Slide 14: 4Q Operation
4Q-Operation

## Slide 15: PQ Operation
PQ-Operation

## Slide 16: Q versus U operation
Q vs. U - Operation

## Slide 17: Current flow through the converter
Current flow through the converter
DC current is divided among three converter phases
AC current is split among the two poles

## Slide 18: Point of Definition for Power
Point of Definition for Power

## Slide 19: Power Flow
Power Flow
Load Flow principles
DC voltage drop
UDC,rec > UDC,Inv
Modulation index principle:
US,rec > US,Inv