## Slide 1: Module 10
Control & Protection

## Slide 2
What can a converter control?
Control values of the fast control loop:
DC voltage
DC current
AC current
                Positive phase active current ip,psf
                Positive phase reactive current iq,psf
                Negative phase active current iq,nsf
                Negative phase reactive current iq,nsf
AC voltage
AC frequency
Converter energy

## Slide 3
Energy flow
Converter has only a limited energy storage capability, so that during the steady state operation the energy of the converter must be balanced over one period
The energy balancing can be done either through the AC side or through the DC side
One side of the converter defines the power flow, the other side is responsible for the balancing

## Slide 4
Basic Control Principle of the HVDC Converter
Control system consists of three major control loops:
AC loop
DC loop
Inner loop
Impedances of the control loop:
AC converter impedance
DC converter impedance
AC grid impedance
DC line impedance
Converter internal impedance

## Slide 5
AC current control
Control input / Control reference:
wconv
ip / P
Control output:
Udc
Scenario:
AC power is defined by the operator
DC voltage is used to control the power flow on the DC side to balance the converter energy

## Slide 6
AC voltage control
Control input / Control reference:
wconv
UAC
fAC
Control output:
Udc
Scenario:
AC power is defined by the AC load
DC voltage is used to control the power flow on the DC side to balance the converter energy

## Slide 7
DC voltage control
Control input / Control reference:
wconv
UDC
Control output:
ip
Scenario:
Station defines the voltage on the DC line
AC current (and therefore AC power) is used to balance the converter energy

## Slide 8
Reactive power control
In control modes without AC voltage and frequency control, the reactive power can be controlled independently if the energy balancing
The reactive power does not require DC power flow and can operate without DC line connected

## Slide 9
AC control
 | AC current source | AC voltage source
 | Grid Following (GFL) P/Q – control mode | V/f or Grid Forming (GFM)
Primary Control Parameters | Active current Reactive current | AC frequency AC voltage
Secondary Control Parameters | Active power Reactive power | 
 | AC voltage | 
Grid application | SCL ≥ 2 | SCL < 2

## Slide 10
Grid Forming Control Concept
Grid-forming Converters
Advantages of grid-forming control in HVDC and FACTS applications
White paper
Siemens Energy

## Slide 11
Steady State power transmission
  One station controls DC voltage
  One station controls active power
  Two active power control modes are possible
    P/Q – Control mode
    U/f – Control mode

## Slide 12
Steady State control principle
  Standard Operation
  Station which sees the highest DC voltage controls the DC voltage
  Active power can be defined at any station
  Wind Farm connection
  Rectifier receives power coming from WTG
  Inverter needs to consider the DC line voltage drop
  Rectifier receives power coming from WTG
  Inverter needs to consider the DC line voltage drop

## Slide 13
Dynamic Analysis
  Dynamic Analysis covers converter behaviour during AC grid faults (faults on the network side of the converter transformer)
  AC grid faults are very common, so that the converter must stay connected to the grid and is required to provide supporting functions
CIGRÉ TB 832: GUIDE FOR ELECTROMAGNETIC TRANSIENT STUDIES INVOLVING VSC CONVERTERS

## Slide 14
Dynamic Analysis: 3ph-to-GND at the inverter
CIGRÉ TB 832: GUIDE FOR ELECTROMAGNETIC TRANSIENT STUDIES INVOLVING VSC CONVERTERS

## Slide 15
Dynamic Analysis: 3ph-to-GND at the rectifier
CIGRÉ TB 832: GUIDE FOR ELECTROMAGNETIC TRANSIENT STUDIES INVOLVING VSC CONVERTERS

## Slide 16
Control hierarchy
CLC/TS 50654-1:2020
HVDC control

## Slide 17
Control requirements
  Input parameters for the control:
    Voltage Measurement
    Current measurement
  Control functions:
    Current control
    Voltage control
  Reference voltage generation for six voltage sources
  Voltage synthetisation by generating switching pulses for individual modules