## Slide 1: Module 02
AC Power Transmission and PSCAD

## Slide 2
Power exchange in AC grid
IEC TR 63363-1:2022

## Slide 3
Power exchange
  For active power transmission reactive power is necessary
  Increase of AC voltage increases the demand of the reactive power
  Changing of power flow direction changes also the reactive power demand
Parameter | Case 1 | Case 2 | Case 3 | Case 4
PS | 1000 MW | 1500 MW | 1000 MW | -1000 MW
UE | 230 kV | 230 kV | 230 kV | 230 kV
US | 232 kV | 232 kV | 240 kV | 232 kV
RS | 0.144 Ω | 0.144 Ω | 0.144 Ω | 0.144 Ω
XS | 1.15 Ω | 1.15 Ω | 1.15 Ω | 1.15 Ω
δ | 1.19° | 1.816° | 1.081° | -1.319°
QS | 288 MVAr | 239 MVAr | 905 MVAr | 541 MVAr

## Slide 4
Power exchange
  Active power transmission is done by phase difference variation
  Reactive power transmission is done by voltage amplitude

## Slide 5
Power Transmission in AC grid
  Principles of AC power transmission are demonstrated with a simple AC network
  Grid is connected to the load with the impedance ZL via an AC cable with length Lcable

## Slide 6
Transmission line is represented by 2-port units
  AC line can be represented by a π-section model
  AC cables are dominated by capacitances
  AC overhead lines (OHL) are dominated by inductances
Parameter |  | OHL | Cable (XLPE)
C’L | nF/km | 10 | 180 - 420
R’L | Ω/km | 0.1 - 1 | 0.1 - 1
X’L | mH/km | 1 | 0.31 – 1.42
G’L | μS/km | 0.05 | 1
  Cable Parameters for following examples:
  C’L = 190 nF/km
  R’L = 22 mΩ/km
  X’L = 1.35 mH/km

## Slide 7
Power Transmission in AC grid
  No Load is connected to the AC line
  Connection of an AC cable creates a significant current flow and reactive power demand
Parameter | Value
US, L-L | 230 kV 1.0 p.u
IS | 1060 A
PS | 2.2 MW
QS | -421 MVAr
UR, L-L | 1.22 p.u.
IR | 0 A
PR | 0 MW
QR | 0 MVAr
Lcable | 60 mi

## Slide 8
Power Transmission in AC grid
  AC grid operator would usually not allow an uncompensated AC cable connection
  Reactive power compensation with a shunt reactor with the rating Qcomp is usually required
Parameter | Value
US, L-L | 230 kV 1.0 p.u
IS | 40 A
PS | 2.2 MW
QS | -14.4 MVAr
UR, L-L | 1.22 p.u.
IR | 830 A
PR | 0 MW
QR | -277 MVAr
Lcable | 60 mi
Qcomp | 400 MVAr

## Slide 9
Power Transmission in AC grid
  Power transmission decreases the voltage increase
  Decreased reactive power demand
Parameter | Value
US, L-L | 230 kV 1.0 p.u
IS | 1340 A
PS | 511 MW
QS | -150 MVAr
UR, L-L | 1.06 p.u.
IR | 1180 A
PR | 500 MW
QR | 0 MVAr
Lcable | 60 mi

## Slide 10
Power Transmission in AC grid

## Slide 11
Transmission line is represented by 2-port units
  Wave impedance
  Propagation level:
  Voltage calculation along the line
  2-port parameters calculations

## Slide 12
Link collection
  Over Head Line (OHL) conductor data:
      https://www.southwire.com/wire-cable/bare-aluminum-overhead-transmission-distribution/c/c-bare-aluminum-overhead
  AC Cable data:
  https://new.abb.com/docs/default-source/ewea-doc/xlpe-submarine-cable-systems-2gm5007.pdf
  PSCAD Tutorials and information
  https://www.pscad.com/knowledge-base/topic-281/v-
  https://www.pscad.com/knowledge-base/article/44