## Slide 1: Module 04
MMC Converter

## Slide 2
Modular Multilevel Converter (MMC)
Energy storage elements are distributed Submodules (SM)
No series connection of IGBTs  IGBTs are not switched at the same time
Reduced switching impulses

## Slide 3
Modular Multilevel Converter (MMC)
Voltage creation by switching on and off the capacitors
Assuming the voltage steps are small enough, any voltage shape can be created
With the 3.3 kV IGBT, a capacitor voltage of ~ 2kV can be assumed

## Slide 4
Controllable Voltage Source
Voltage converter consists of six controllable voltage sources
Voltage sources can be controlled independently

## Slide 5
Converter Terminology IEC 62747:2014
2- and 3-Level converter
MMC converter

## Slide 6
MMC – Voltage Creation
  + 4kV
  - 4kV
  Assumption: Ucap = 2kV
  Uvalve_p = 6 kV
  Uvalve_n = 2 kV
  Udpp = 8 kV
  Uve = -2 kV
  Uvalve_p = 4 kV
  Uvalve_n = 4 kV
  Udpp = 8 kV
  Uve = 0 kV
  Uvalve_p = 2 kV
  Uvalve_n = 6 kV
  Udpp = 8 kV
  Uve = +2 kV

## Slide 7
Controllable Voltage Source

## Slide 8
Controllable Voltage Source

## Slide 9
Controllable Voltage Source

## Slide 10
Controllable Voltage Source

## Slide 11
Modulation Index

## Slide 12
Modularization
Higher DC voltage can be reached by connecting additional SMs in series or by using SMs with higher voltage capability  Other IGBT types
For higher currents other IGBTs must be used  Other SMs

## Slide 13
Submodule set-up
Submodule is a device which is capable to switch on or off the individual capacitor voltage at its terminal
Additional elements are:
      Thyristor
      Bypass Switch
Submodule

## Slide 14
Operating conditions
Operating Conditions of Half Bridge Submodule

## Slide 15
Redundancy concept
Submodule redundancy is achieved by mechanical bypass switch
In case of a submodule fault the bypass switch is closed creating a low resistance short circuit of the SM
Mechanical bypass switch

## Slide 16
AC side voltage

## Slide 17
Module Voltage

## Slide 18
Module Current

## Slide 19
Module Power and Energy

## Slide 20
Module Energy
  SM has negative voltage, which is physically not possible
  SM is discharged to zero

## Slide 21
SM voltage
Parameter | Value
CSM | 5 mF
Usm_max | 2000 V
NSM | 200, 400
  NSM = 200

## Slide 22
SM and valve voltage
  NSM = 200
  NSM = 400

## Slide 23
SM and valve voltage
  NSM = 200
  NSM = 400

## Slide 24
SM to valve voltage
  SM are used not just to store energy for power transmission but also for module voltage generation
  At any point the sum of the SM voltage must be higher than the requested module voltage
  The relation between sum of SM and the required module voltage is called inner modulation index a
  a

## Slide 25
P2000DL45X168
Relevant data from IGBT data sheet

## Slide 26
infineon.com
HVDC VALVES Power Electronics for HVDC Schemes
2019, General Electric Company

## Slide 27
https://www.hitachienergy.com/ca/fr/news/press-releases/2021/12/hitachi-energy-wins-major-contract-for-the-first-of-its-kind-sub-sea-power-transmission-network-in-the-mena-region-advancing-a-sustainable-energy-future-for-abu-dhabi
https://www.ge.com/news/taxonomy/term/6426